## liquefied gas
The calculation of percentage of oxygen in the air after the evaporation of a volume of liquefied gas - either nitrogen or argon
Room volume
Length (metres) | 0 | The room dimensions
Width (metres) | 0
Height (metres) | 0
Room Volume (l*w*h) | 0
Volume of gas produced by evaporating liquid Nitrogen
Volume of Liquid Nitrogen (litres) | 0 | The volume of liquid NITROGEN involved
Volume of gas produced (Voll*682.5) (litres) | 0 | [liquid volume] times [expansion factor] (ref BOC data sheet)
Volume of gas produced (metre3)(Volgas/1000) | 0 | volume converted to cubic metres
Volume of gas produced by evaporating liquid Argon
Volume of Liquid Argon (litres) | 0 | The volume of liquid ARGON involved
Volume of gas produced (Vol*824.3) (litres) | 0 | [liquid volume] times [expansion factor] (ref BOC data sheet)
Volume of gas produced (metre3)(Volgas/1000) | 0 | volume converted to cubic metres
Percentage oxygen in room for NITROGEN evaporation
Vol0 0.2095([Room Vol]-[Vol gas produced] | 0 | Volume of oxygen = [fraction of oxygen in air] times ([the volume of the room] - [ volume of nitrogen liberated])
%O2 (100*[VolO]/[Room vol] | #DIV/0! | Volume of oxygen divided by the room volume times 100
Percentage oxygen in room for ARGON evaporation
Vol0 0.2095([Room Vol]-[Vol gas produced] | 0 | Volume of oxygen = [fraction of oxygen in air] times ([the volume of the room] - [ volume of argon liberated])
%O2 (100*[VolO]/[Room vol] | #DIV/0! | Volume of oxygen divided by the room volume times 100
Instructions
Fill in the white boxes with the appropriate figures and read the percentage of oxygen remaining in the room in the red box.
Note
This assumes that there is no dilution due to fresh air being pumped into the room and does not allow for the
volume of any furniture or people in the room
ref: based on a calculator by BOC

## cylinder gas
The calculation of percentage of oxygen in the air after release of cylinder gas
Room volume
Length (metres) | 0 | The room dimensions
Width (metres) | 0
Height (metres) | 0
Room Volume (l*w*h) | 0
Volume of gas released
Volume of gas [Litres] | 0 | cylinder contents at NTP
Volume of gas produced (Metre3) (Volgas/1000) | 0 | volume converted to cubic metres
Percentage oxygen in room
Vol0 0.2095([Room Vol]-[Vol gas produced] | 0 | Volume of oxygen = [fraction of oxygen in air] times ([the volume of the room] - [ volume of nitrogen liberated])
%O2 (100*[VolO]/[Room vol] | #DIV/0! | Volume of oxygen divided by the room volume times 100
Fill in the white boxes and read the percentage of oxygen from the red box. Assumptions - even mixing of gas in the room and no allowances for fittings and persons in the room.
ref: based on a calculator by BOC